## Slide 1
Steam Distribution
System
Notes: TO THE TRAINER
This PowerPoint presentation can be used to train people about the basics of steam. The information on the slides is the minimum information that should be explained. The trainer notes for each slide provide more detailed information, but it is up to the trainer to decide if and how much of this information is presented also.
Additional materials that can be used for the training session are available on www.energyefficiencyasia.org under “Energy Equipment” and include:
Textbook chapter on this energy equipment that forms the basis of this PowerPoint presentation but has more detailed information
Quiz – ten multiple choice questions that trainees can answer after the training session
Workshop exercise – a practical calculation related to this equipment
Option checklist – a list of the most important options to improve energy efficiency of this equipment
Company case studies – participants of past courses have given the feedback that they would like to hear about options implemented at companies for each energy equipment. More than 200 examples are available from 44 companies in the cement, steel, chemicals, ceramics and pulp & paper sectors

## Slide 2
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment
Steam Distribution System

## Slide 3
About 80% electricity is produced by steam in the whole world.
In Pakistan, thermal power accounts for 64 per cent of the total energy production.
So, energy Management in steam distribution system is very important.
INTRODUCTION

## Slide 4
Steam Distribution System
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment

## Slide 5: Steam Distribution System
Link between steam generator and point of use
Steam generator
  Boiler
  Discharge from co-generation plant
Boilers use
  primary fuel
  exhaust gases
What is the steam distribution system?
Notes: The steam distribution system is the essential link between the steam generator and the steam user. There are various methods to carry steam from a central source to the point of use. The central source might be a boiler house or the discharge from a co-generation plant. The boilers may burn primary fuel, or be waste heat boilers using exhaust gases from high temperature processes, engines or even incinerators.

## Slide 6
Typical steam circuit
Steam Distribution System
Notes: An understanding of the basic steam circuit or ‘steam and condensate loop’ is required
Note to the trainer: a detailed description is in the chapter. Below are the summarized points only
As steam condenses in a process, flow is induced in the supply pipe.
The steam generated in the boiler must be conveyed through main pipes, or 'steam mains‘ and then smaller branch pipes.
Heat is transferred from the steam to the pipe, so the pipework will begin to transfer heat to the air.
Steam on contact with the cooler pipes will begin to condense immediately. On start-up of the system, the condensing rate will be at its maximum and is commonly called the ‘starting load’. Once the pipework has warmed up, the condensing rate is minimal and commonly called the ‘running load’.
The resulting condensation (condensate) falls to the bottom of the pipe and will then have to be drained from various strategic points in the steam main.
When the valve on the steam pipe serving an item of steam using plant is opened, steam flowing from the distribution system enters the plant and again comes in contact with cooler surfaces. The steam then transfers its energy in warming up an equipment and product (starting load), and, when up to temperature, continues to transfer heat to the process (running load).
There is now a continuous supply of steam from the boiler.
More water (and fuel to heat this water) is supplied to the boiler to make up for the water which has previously been evaporated into steam. The condensate formed in both the steam distribution pipework and in the process equipment is a convenient supply of useable hot boiler feedwater.

## Slide 7
Pipes
Drain points
Branch lines
Strainers
Filters
Separators
Most important components
Steam traps
Air vents
Condensate recovery system
Insulation
Steam Distribution System
Notes: We will now explain the most important components of a steam distribution system

## Slide 8
Pipe material: carbon steel or copper
Correct pipeline sizing is important
Oversized pipe work:
  Higher material and installation costs
  Increased condensate formation
Undersized pipe work:
  Lower pressure at point of use
  Risk of steam starvation
  Risk of erosion, water hammer and noise
1. Pipes
Steam Distribution System
Notes: Pipe material: Pipes for steam systems are commonly manufactured from carbon steel to ANSI B 16.9 Al06. The same material may be used for condensate lines, although copper tubing is preferred in some industries. For high temperature superheated steam mains, additional alloying elements, such as chromium and molybdenum, are included to improve tensile strength and creep resistance at high temperatures. Typically, pipes are supplied in 6-meter lengths.
Pipeline sizing: The objective of the steam distribution system is to supply steam at the correct pressure to the point of use. Pipeline sizing is an important factor.
Oversized pipework means:
  Pipes, valves, fittings, etc. will be more expensive than necessary.
  Higher installation costs will be incurred, including support work, insulation, etc.
  For steam pipes a greater volume of condensate will be formed due to the greater heat loss. This in turn means that either more steam trapping is required or wet steam is delivered to the point of use.
Undersized pipework means:
  A lower pressure may only be available at the point of use. This may hinder equipment performance due to only lower pressure steam being available.
  There is a risk of steam starvation.
  There is a greater risk of erosion, water hammer and noise due to the inherent increase in steam velocity.
The required pipeline size can be calculated based on pressure drop and velocity. Note to the trainer: if time allow you can use the chapter to explain how each of these calculation methods work

## Slide 9
Ensures that condensate can reach steam trap
Consideration must be give to
  Design
  Location
  Distance between drain points
  Condensate in steam main at shutdown
  Diameter of drain pipe
2. Drain points
Steam Distribution System
Notes: The drain point must ensure that the condensate can reach the steam trap.
Careful consideration must be given to
  the design of the drain points
  Location of the drain points
  Distance between drain points. The amount of condensate formed in a large steam main under start-up conditions is sufficient to require the provision of drain points at intervals of 30m to 50m, as well as natural low points such as at the bottom of rising pipework.
  Condensate remaining in a steam main at shutdown, when steam flow ceases. Gravity will ensure that the water (condensate) will run along sloping pipework and collect at low points in the system. Steam traps should therefore be fitted to these low points.
  Diameter of the drain pipe (discussed on next slides)

## Slide 10
3. Branch lines
Take steam away from steam main
Shorter than steam mains
Pressure drop no problem if branch line < 10 m
A Branch Line
Steam Distribution System
Notes: Branch lines are normally much shorter than steam mains. As a general rule, therefore, provided the branch line is not more than 10 metres in length, and the pressure in the main is adequate, it is possible to size the pipe on a velocity of 25 to 40 m/s, and not to worry about the pressure drop

## Slide 11
Purpose
  Stop scale, dirt and other solids
  Protect equipment
  Reduce downtime and maintenance
Fitted upstream of steam trap, flow meter, control valve
Two types: Y-type and basket type
4. Strainers
Steam Distribution System
Notes: In steam and condensate systems, damage to plant is frequently caused by pipeline debris such as scale, rust, jointing compound, weld metal and other solids, which may find their way into the pipeline system.
Strainers are devices which arrest these solids in flowing liquids or gases, and protect equipment from their harmful effects, thus reducing downtime and maintenance. A strainer should be fitted upstream of every steam trap, flow meter and control valve.
Strainers can be classified into two main types according to their body configuration; namely the Y-type and the basket type. Typical examples of these types of strainers can be seen in Figure 14.

## Slide 12
Consists of sintered stainless steel filter element
Remove smallest particles
  Direct steam injection – e.g. food industry
  Dirty stream may cause product rejection – e.g. paper machines
  Minimal particle emission required from steam humidifiers
  Reduction of steam water content
5. Filters
Steam Distribution System
Notes: A filter used in a steam system typically consists of a sintered stainless steel filter element.
Filters are used to remove smaller particles than strainers, for example, in the following applications:
When there is direct injection of steam into a process, which may cause contamination of the product. Example: In the food industry, and for the sterilization of process equipment in the pharmaceutical industry.
Where dirty steam may cause rejection of a product or process batch due to staining or visible particle retention. Example: Sterilizers and paper/board machines.
Where minimal particle emission is required from steam humidifiers. Example: Humidifiers used in a “clean” environment.
For the reduction of the steam water content, ensuring a dry, saturated supply.

## Slide 13
Separators remove suspended water droplets from steam
Water in steam causes problems
  Water is barrier to heat transfer
  Erosion of valve seals and fittings and corrosion
  Scaling of pipe work and heating surfaces from impurities
  Erratic operation and failure of valves and flow meters
6. Separators
Steam Distribution System
Notes: Separators are used to remove suspended water droplets from steam. The presence of water in steam can cause a number of problems:
As water is an extremely effective barrier to heat transfer, its presence can reduce plant productivity and product quality.
Water droplets travelling at high steam velocities will erode valve seals and fittings, a condition known as wiredrawing. The water droplets will also increase the amount of corrosion.
Increased scaling of pipework and heating surfaces from the impurities carried in the water droplets.
Erratic operation of control valves and flow meters.
Failure of valves and flow meters due to rapid wear or water hammer.
There are three types of separators: baffle type, cyclonic type and coalescence type

## Slide 14
What is a steam trap?
  “Purges” condensate out of the steam system
  Allows steam to reach destination as dry as possible
Steam traps must handle variations in
  Quantity of condensate
  Condensate temperature
  Pressure (vacuum to > 100 bar)
7. Steam traps
Steam Distribution System
Notes: No steam system is complete without that crucial component 'the steam trap' (or trap). This is the most important link in the condensate loop because it connects steam usage with condensate return. A steam trap quite literally 'purges' condensate, (as well as air and other incondensable gases), out of the system, allowing steam to reach its destination in as dry a state/condition as possible to perform its task efficiently and economically.
The quantity of condensate a steam trap has to deal with may vary considerably. It may have to discharge condensate at steam temperature (i.e. as soon as it forms in the steam space) or it may be required to discharge below steam temperature, giving up some of its 'sensible heat' in the process.
The pressures at which steam traps can operate may be anywhere from vacuum to well over a hundred bar.

## Slide 15
Effect of air on heat transfer
8. Air vents
Steam Distribution System
Notes: If air is mixed with steam and flows along with it, pockets of air will remain at the heat exchange surfaces where the steam condenses. Gradually, a thin layer builds up to form an insulating blanket, hindering heat transfer as shown in the figure on this slide.
A film of air only 1 mm thick offers about the same resistance to heat flow as a wall of copper some 15 meters thick!
When air is added to steam, the heat content of a given volume of the mixture is lower than the same volume of pure steam, so the mix temperature is lowered. Hence, the presence of air has a double effect:
  It offers a resistance to heat transfer via its layering effect
  It reduces the temperature of the steam space thus reducing the temperature gradient across the heat transfer surface

## Slide 16
What is condensate
  Distilled water with heat content
  Discharged from steam plant and equipment through steam traps
Condensate recovery for
  Reuse in boiler feed tank, deaerator or as hot process water
  Heat recovery through heat exchanger
9. Condensate recovery system
Steam Distribution System
Notes: When a kilogram of steam condenses completely, a kilogram of condensate is formed at the same pressure and temperature. As well as having heat content, the condensate is basically distilled water, which is ideal for use as boiler feedwater.
An efficient steam system will collect this condensate and either return it to a deaerator, a boiler feedtank, or use it in another process. Only when there is a real risk of contamination should condensate not be returned to the boiler. Even then, it may be possible to collect the condensate and use it as hot process water or pass it through a heat exchanger where its heat content can be recovered before discharging the water mass to drain.

## Slide 17
Temperature | Application | Materials
Low (<90 oC) | Refrigerators, cold / hot water systems, storage tanks | Cork, wood, 85% magnesia, mineral fibers, polyurethane, expanded polystyrene
Medium (90 – 325 oC) | Low-temperature heating and steam generating equipment, steam lines, flue ducts, | 85% magnesia, asbestos, calcium silicate, mineral fibers
High (>325 oC) | Boilers, super-heated steam systems, oven, driers and furnaces | Asbestos, calcium silicate, mineral fibre, mica, vermiculite, fireclay, silica, ceramic fibre
10. Insulation
Classification of insulators
Steam Distribution System
Notes: Insulators can be classified based on the three temperature ranges for which they are used:
Low Temperature Insulators (up to 90oC), which are used for refrigerators, cold and hot water systems, storage tanks, etc. The most commonly used materials are cork, wood, 85 percent magnesia, mineral fibres, polyurethane and expanded polystyrene
Medium Temperature Insulators (90 – 325oC), which are used in low-temperature heating and steam generating equipment, steam lines, flue ducts, etc. The most commonly used materials include 85 percent magnesia, asbestos, calcium silicate and mineral fibres
High Temperature Insulators (325oC and above), which are typically used for boilers, super-heated steam systems, oven, driers and furnaces. The most commonly used materials are asbestos, calcium silicate, mineral fibre, mica, vermiculite, fireclay, silica and ceramic fibre.

## Slide 18
Assessment of steam distribution
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment

## Slide 19
Assessment of steam distribution
Waste heat sources and their uses can be conveniently categorized by the temperature at which the heat is exhausted, as shown in Table

## Slide 20
Assessment of steam distribution
The use of waste heat to heat a fluid stream should be considered if:
The waste heat source is close enough to the fluid stream that the fluid temperature will still be high enough to be useful even after taking into account all heat lost in transporting the fluid from source to stream.
Using waste heat from the source will not create problems at the source.
The transfer of heat from the source to the stream is technically feasible.

## Slide 21
Assessment of steam distribution

## Slide 22
Energy Efficiency Opportunities
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment

## Slide 23
Manage steam traps
Avoid steam leaks
Provide dry steam for process
Utilize steam at lowest acceptable pressure
Proper utilization of directly injected steam
Minimize heat transfer barriers
Minimize water hammer
Insulate pipelines and equipment
Improve condensate recovery
Recover flash steam
Reuse low pressure steam
Energy Efficiency Opportunities
Notes: There are many areas for energy efficiency opportunities in the steam distribution system. We will now go through the most important opportunities

## Slide 24
Testing of steam traps
  Visual: flow and flow variations
  Sound: check sound created by flow
  Temperature: discharge temperature on outlet
  Integrated: measures conductivity
Routine maintenance
Replacement of internal parts
Replacement of traps
1. Manage steam traps
Energy Efficiency Opportunities
Notes: Energy losses can be reduced using steam traps, provided attention is giving to the following areas:
Testing of steam traps (the text on the slides should be sufficient for the session. The full text from the book is included below but it depends on time whether all information can be explained)
  Visual: Visual testing of the flow or variation of flow of steam traps makes use of sight glasses, sight checks, test tees and three-way test valves. This method works well with traps that have an on/off cycle or low flows. This method becomes less viable when the flow, and thus the volume of water and flash steam, is high
  Sound: Sound testing makes use of ultrasonic leak detectors, mechanics stethoscopes, screwdriver or a metal listening rod. These methods use the sound created by flow to determine if the trap is functioning properly. This method works well with traps that have an on/off cycle or low flows, but not so well with traps with varying and/or high flows
  Temperature: Temperature testing makes use of infrared guns (see Monitoring Equipment chapter), surface pyrometers, temperature tapes, and temperature crayons. These equipment measure the discharge temperature on the outlet side of the trap, with high temperatures indicating leaks and low temperatures indicating blocked, undersized, or faulty traps.
  Integrated: Spirax Sarco mentions the development of an integrated steam trap testing device due to the limitations of the above methods. This consists of a sensor, fitted inside the steam trap, which is capable of detecting the physical state of the medium at that point by conductivity. This
Routine maintenance, which depends on the type of trap and its application.
Replacement of internals. The renewal of internal parts of a steam trap makes good sense. The body will generally have as long a life as the plant to which it is fitted and it is only the internal parts which wear, depending on system conditions. There are obvious advantages in replacing these internals from time to time. It depends on the ease with which the new parts can be fitted and the reliability and availability of the refurbished trap.
Replacement of traps. On occasions, it will be easier and cheaper to replace traps rather than repair them. In these cases it is essential that the traps themselves can be changed easily. Flanged connections provide one solution, although the flanged trap is more expensive than the equivalent screwed trap. Mating flanges are an additional expense.

## Slide 25
Repair leaks
Regular leak detection program
Replace flanged joints by welded joints
Leakage estimate
  Plume length 1400 mm
  Steam loss 40 kg/hr
2. Avoid steam leaks
Energy Efficiency Opportunities
Notes: Steam leaks are a source of energy loss and must be avoided.
It is estimated that a 3 mm diameter hole on a pipeline carrying 7kg/cm2 steam would waste 33 kL of fuel oil per year.
Steam leaks on high-pressure mains are prohibitively costlier than on low pressure mains.
T avoid steam leaks, a plant should
Repair leaks immediately
Have a regular surveillance programme for identifying leaks at pipelines, valves, flanges and joints.
Replace the flanged joints which are rarely opened in old plants by welded joints.
(Click once) The figure provides a quick estimate for steam leakage based on plume length. For example, if the plume length is 700 mm then the steam loss is 10 kg/h

## Slide 26
Dry saturated steam is best steam
  Wet steam reduces total heat in steam and prevents heat transfer
  Superheated steam gives up heat at slower rate
Achieve dry steam by
  Proper boiler treatment
  Boiler operation
  Pipeline insulation
  Separators on steam pipelines
3. Provide dry steam for process
Energy Efficiency Opportunities
Notes: The best steam for industrial process heating is the dry saturated steam.
  Wet steam reduces total heat in the steam. Also water forms a wet film on heat transfer and overloads traps and condensate equipment. Wet steam can reduce plant productivity and product quality, and can cause damage to most items of plant and equipment.
  Superheated steam is not desirable for process heating because it gives up heat at a rate slower than the condensation heat transfer of saturated steam.
It must be remembered that a boiler without a superheater cannot deliver perfectly dry saturated steam. At best, it can deliver only 95 to 98 percent dry steam. The dryness fraction of steam depends on various factors, such as the level of water in the boiler. The dryness of the steam can be maximized by
  Proper boiler water treatment
  Boiler operation
  Lagging of the pipelines
  Separators in steam pipelines to remove suspended water droplets, separators are installed in steam pipelines

## Slide 27
Steam should be
  Generated & distributed at highest pressure
  Utilized at lowest pressure: latent heat highest
Select lowest steam pressure without sacrificing
  Production time
  Steam consumption
4. Utilize steam at lowest acceptable pressure
Energy Efficiency Opportunities
Notes: 4. Utilize steam at the lowest acceptable pressure for the process
As a guide, the steam should always be generated and distributed at the highest possible pressure, but utilized at as low a pressure as possible since it then has higher latent heat.
There is a limit to the reduction of steam pressure. Depending on the equipment design, the lowest possible steam pressure with which the equipment can work should be selected without sacrificing
  Production time: it may also be seen from the steam tables that the lower the steam pressure, the lower will be its temperature. Since temperature is the driving force for the transfer of heat at lower steam pressures, the rate of heat transfer will be slower and the processing time greater
  Steam consumption: In equipment where fixed losses are high (e.g. big drying cylinders), there may even be an increase in steam consumption at lower pressures due to increased processing time.

## Slide 28
Benefits
  Equipment simple, cheap and easy to maintain
  No condensate recovery system needed
  Heating quick and process thermally efficient
Only in processes were dilution is not a problem
5. Proper utilization of directly injected steam
Energy Efficiency Opportunities
Notes: 5. Proper utilization of directly injected steam
The heating of a liquid by direct injection of steam is often desirable.
The equipment required is relatively simple, cheap and easy to maintain.
No condensate recovery system is necessary.
The heating is quick, and the sensible heat of the steam is also used up along with the latent heat, making the process thermally efficient.
In processes where dilution is not a problem, heating is done by blowing steam into the liquid, i.e. direct steam injection is applied. If the dilution of the tank contents and agitation are not acceptable in the process, i.e. direct steam agitation is not acceptable, indirect steam heating is the only answer.

## Slide 29
Temperature gradient across heat transfer barriers
6. Minimize heat transfer barriers
Energy Efficiency Opportunities
Notes: 6. Minimize heat transfer barriers
Heat transfer barrier are shown in the figure: The metal wall may not be the only barrier in a heat transfer process. There is likely to be a film of air, condensate and scale on the steam side. On the product side there may also be baked-on product or scale, and a stagnant film of product. (Point at each barrier on the figure)

## Slide 30
Banging noise caused by colliding condensate in distribution system
Sources: low points in the pipework
Solutions
  Steam lines with gradual fall in flow direction
  Drain points at regular intervals
  Check valves after all steam traps
  Opening isolation valves slowly to drain condensate
7. Minimize water hammer
Energy Efficiency Opportunities
Notes: Waterhammer is the noise caused by slugs of condensate colliding at high velocity into pipework fittings, plant, and equipment.
Indications of waterhammer include a banging noise, and perhaps movement of the pipe. In severe cases, waterhammer may fracture pipeline equipment with almost explosive effect, with consequent loss of live steam at the fracture, leading to an extremely hazardous situation.
Commonly, sources of waterhammer occur at the low points in the pipework, for example, sagging in the line, perhaps due to failure of supports.
To summarize, the possibility of waterhammer is minimized by:
  Installing steam lines with a gradual fall in the direction of flow, and with drain points installed at regular intervals and at low points.
  Installing check valves after all steam traps, which would otherwise allow condensate to run back into the steam line or plant during shutdown.
  Opening isolation valves slowly to allow any condensate, which may be lying in the system to flow gently through the drain traps, before it is picked up by high velocity steam. This is especially important at start-up.

## Slide 31
8. Insulation
Costs of insulation
Heat loss savings
Economic Thickness of Insulation (ETI)
Energy Efficiency Opportunities
Notes: What insulation is, the benefits and types of insulation options were already explained as part of the steam distribution system. An important factor in determining if insulation or improved insulation is a good energy efficiency option is the costs. For this reason we will explain how to determine if insulation is cost effective.
The effectiveness of insulation follows the law of decreasing returns. This means that insulation results in energy and cost savings, but with increasing thickness of insulation the additional amount of energy and cost saved is going down.
The figure shows this:
(Click once) the costs of insulation per m2 of surface rises with increasing insulation thickness
(Click once) the heat savings per m2 of insulated surfaces decreases with increasing insulation thickness
(Click once) At a certain level, any additional insulation is no longer economically justifiable. The point where the amount of insulation gives the greatest return on investment is called the “economic thickness of insulation” (ETI) and is shown in the figure.
The ETI is calculated based on the following factors, which differ between companies:
Cost of fuel
Annual hours of operation
Heat content of fuel
Boiler efficiency
Operating surface temperature
Pipe diameter/thickness of surface
Estimated cost of insulation.
Average exposure ambient still air temperature
Note: a calculation method (section 3.2.2) and example (section 3.2.3) is included in the chapter but will not be explained as part of this session

## Slide 32
9. Improved condensate recovery
Annual condensate recovered (kg/yr)
Heat recovered (kcal/yr)
Heat saved (kcal/yr)
Fuel saved (litres or m3 /yr)
$ saved ($ /yr)
Energy Efficiency Opportunities
Notes: Calculating the amount of money saved from condensate recovery allows you to determine further potential savings from improved condensate recovery.
The savings from condensate recovery can be calculated as follows:
Calculate the annual quantity of condensate recovered in kg/yr
Calculate the heat recovered by converting the kg/yr to kcal/yr
Calculate the heat saved in kcal/yr by multiplying the heat recovered by the boiler efficiency, e.g. 80%
Calculate the amount of fuel (coal, fuel oil or gas) saved by multiplying the heat saved with the calorific value of fuel
Calculate the amount of money saved by multiplying the amount of fuel with the cost of fuel

## Slide 33
Flash steam released from hot condensate when pressure reduced
Amount available: calculation or tables/charts
Applications: heating
Boiler blowdown can also be recovered as flash steam
10. Recover flash steam
Energy Efficiency Opportunities
Notes: Flash steam is released from hot condensate when its pressure is reduced. As an example, when steam is taken from a boiler and the boiler pressure drops, some of the water content of the boiler will flash off to supplement the ‘live’ steam produced by the heat from the boiler fuel.
If use is to be made of flash steam, it is helpful to know how much of it will be available. The quantity is readily determined by calculation, or can be read from simple tables or charts.
Typical applications of flash steam include heating (with air heater batteries and space heating installations using either radiant panels or unit heaters), steam heated hot water calorifier and a steam to water calorifier. Boiler blowdown can also be recovered as flash steam, as is explained in the separate Boiler Chapter.

## Slide 34
Reuse as water
Compress with high pressure steam for reuse as medium pressure steam
11. Reuse low pressure steam
MOTIVE STEAM H.P.
DISCHARGE STEAM
M.P.
SUCTION STEAM L.P.
Thermo-compressor
Energy Efficiency Opportunities
Notes: In many cases, very low pressure steam is reused as waIn many cases, very low pressure steam is reused as water after condensation when there is no better reuse option. In many cases it becomes feasible to compress this low pressure steam with very high pressure steam and reuse it as a medium pressure steam. The major energy in steam is in its latent heat value and thus thermo-compression would give a large improvement in waste heat recovery. The thermo-compressor (Figure 50) is a simple equipment with a nozzle where HP steam is accelerated into a high velocity fluid. This entrains the LP steam by momentum transfer and then recompresses in a divergent venturi. It is typically used in evaporators where the boiling steam is recompressed and used as heating steam.ter after condensation when there is no better reuse option.
In many cases it becomes feasible to compress this low pressure steam with very high pressure steam and reuse it as a medium pressure steam. The major energy in steam is in its latent heat value and thus thermo-compression would give a large improvement in waste heat recovery.
The thermo-compressor (see figure) is a simple equipment with a nozzle where HP steam is accelerated into a high velocity fluid. This entrains the LP steam by momentum transfer and then recompresses in a divergent venturi. It is typically used in evaporators where the boiling steam is recompressed and used as heating steam.

## Slide 35
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment
Economics of Waste Heat Recovery

## Slide 36
Economics of Waste Heat Recovery
The benefits from waste heat recovery can be substantial; therefore the benefits included in the economic analysis must be as complete as possible

## Slide 37
Economics of Waste Heat Recovery
The analysis must also include complete details of the costs involved and the amount by which these costs are reduced by any tax benefits

## Slide 38
Economics of Waste Heat Recovery
The analysis must also include complete details of the costs involved and the amount by which these costs are reduced by any tax benefits

## Slide 39
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities
The Economics of Waste Heat Recovery
Waste Heat Recovery Equipment
Waste Heat Recovery Equipment

## Slide 40
Waste Heat Recovery Equipment
The factors that determine which equipment to select for waste heat recovery are
The fluid temperature at the source
The intended use for the waste heat, and
The distance the heated fluid (if any) must be transported